WELLHEAD PROTECTION COMMITTEE MEETING – December 18, 2024

Shrewsbury Borough Municipal Building, 35 W. Railroad Ave., Shrewsbury – 7:00 p.m.

Present:  Brian L. Sweitzer, Chairman; Jeff Rennoll, Shrewsbury Township Supervisor; Dan Sipe, resident; Amber Brose, resident(Zoom); Alexis Morris, resident; David Pergrin, resident; Richard Buchanan, resident(Zoom) and Cindy Bosley, Sec.

Others present: Eric Thomas, P.E., Brian Carter, Esq., and Tim Beaver representing Rutters; and Ryan Orgitano from PA Rural Water; John Mock(Zoom)

APPROVAL OF MINUTES

D. Pergrin moved to approve the minutes of the September 20, 2023 and the October 16, 2024 meetings.

D. Sipe seconded.  The motion carried with all voting in favor.

NEW BUSINESS

Update Source Water Protection Plan

Ryan Orgitano of PA Rural Water was present to say there is an opportunity for the Borough to update its 20 year old plan that will include better delineations. Some of the well permits have changed since that time as well. This would be done with a grant from DEP and will be overseen by PA Rural Water.  The cost and the grant would be between $8,000 and 10,000 with no matching cost to the Borough.

D. Pergrin moved to recommend approval to Council that the current plan be updated at no cost to the Borough.

A. Morris seconded.  The motion carried with all voting in favor.

Rutter’s Expansion 249 North Main Street Zone 2

Rutter’s would like to expand into the adjacent lot to the south.  There are currently two 15,000 gallon fuel tanks and they would be replaced with two double-walled tanks and piping with one holding 20,000 gallons of regular fuel and the other one holding 10,000 gallons of premium fuel.  The gasoline from the two tanks would be blended to create the medium grade of gasoline.  The number of fuel pumps will remain the same (four).  The facility profile sheet shows the aggregate bulk storage of regulated substances at 45.49 gallons for the proposed expanded store, well below the 119 gallon maximum storage.  When the tanks are removed, there should be an emergency plan in place.  Items the Committee would like to see on the land development plan:

- An Oil and grease separator on the stormwater system that would be cleaned out every now and then;

- An Emergency Response Plan;

- Double-walled tanks/piping with updated pump technology;

- A gate valve on the storm water system that is marked when and how it should be used;

- See if there is enough room to the rear of the store to create a swale impoundment for surface water before it goes into the storm sewer.

J. Rennoll moved to approve advancement of the proposed expansion with the above five comments included in the land development plan.

A, Morris and R. Buchanan seconded.  The motion carried with all voting in favor.

The reverse subdivision and land development plan will proceed to Staff with the Wellhead Committee reviewing the land development plan.

OLD BUSINESS

95 East Forrest Avenue

AutoZone has suggested that a week’s notice be given by the Borough before an inspection can be made.  The Committee felt the time frame should be 24 hours.

Private Well Inspections

There are five properties in the Township that are connected to York Water and are grandfathered in but have failed to respond to the notice for the five-year inspection.

PFAs Sampling

All of the Borough’s wells meet the State guidelines and B. Sweitzer will continue to monitor and to see if anything changes as far as the EPA guidelines after the new administration takes over.

ADJOURNMENT

D. Sipe moved to adjourn the meeting at 8:03 p.m.

A. Morris seconded.  The motion carried with all voting in favor.

Prepared by Cindy Bosley, Sec.